## Introduction
PNNL-SA-173078
Redundant Water System Runtime Calculator
This Excel-based runtime analysis spreadsheet is a tool to calculate how many days a redundant water system can support its critical loads. It can account for three types of systems:
• Onsite storage tank(s) connected only to the primary water supply,
• Onsite or offsite secondary water source that supplies onsite storage tank(s),
• Onsite or offsite secondary water source that directly supplies critical load(s),
By providing the required information on the "Calculator" tab, the user will get an output estimating the number of days current redundant systems will be able to meet critical loads. Use the system definitions below to check to see if your system meets the criteria of analysis for this tool. If your system does not meet these requirements, the system may be more complex than is able to be modeled in this tool.
System Definitions and Requirements
1. Onsite storage tanks: An onsite storage tank could be connected to only a primary water supply (e.g., municipal or utility) or connected to a secondary, onsite or offsite water source. Whether or not it is additionally connected to the primary supply, if the tank is connected to a secondary supply it falls into the latter category. Rainwater storage tanks are often considered secondary water sources, but for the purpose of this tool, rainwater does not qualify as a secondary source as it is not reliable enough to model as a consistent secondary source. The storage tank itself still counts as a redundent system as the water that is available in the tank can be used during an outage, so the user should select "onsite storage tank(s) connected only to the primary water supply" for rainwater systems with no additional secondary source.
2. Offsite or onsite secondary supply systems: when fully operational, the source is not expected to be exhausted within a reasonable timeframe (e.g., months) and it must be able to continuously provide the design flow rate over the entire duration of the outage. An onsite secondary water source, such as a well, aquifer, or lake, should have enough capacity such that it can be considered infinite for the purpose of this model. Similarly, an offsite secondary water source, such as a regional water tower or industrial-grade storage facility that can supply the site in the case of an outage to the primary municipal water supply, must not be exhausted by the typical demand of the site and other sites that may be expected to draw upon the source during an outage event. If these systems have limited capacity, such as if the supply is dependent on other customers' usage, a more complex model should be pursued instead of this tool.
3. Offsite secondary supply systems: An offsite secondary redundant system must not have any known co-locations or shared vulnerabilities with the primary water system. This could include shared distribution pipe infrastructure, shared reliance on a substation, or shared water source supply. These types of shared systems increase the likelikhood that the redundant system is vulnerable to the same outage events as the primary system.
4. All systems: The site must provide the ability to achieve the appropriate water quality that is required for the site and critical loads, such as potable water or ultra-pure water. Necessary treatment methods should be conducted at the load in case the redundant supply does not meet those standards.
5. Storage tanks: The amount of residual disinfectant (e.g., chlorine) in the water, both in the storage tank and throughout the distribution network, should meet the criteria described in AWWA Manual 20 or equivalent standard, both during regular use and during an outage. The amount of residual disinfectant will be dependent on the tank management, pressure, and network characteristics. Residual disinfectant must be maintained for potable water or non-potable water that comes into contact with humans. Some strategies to maintain proper levels of residual disinfectant include periodic cleaning, cycling water through the tank, aeration, or chemical dosing.
6. Estimating storage tank capacity: The following values are used to define an onsite storage tanks' capacity: "Useable volume", "dead volume", "reserved volume", and "empty volume". Use the diagram below to understand what these values refer to.
• Useable volume: The storage capacity of the tank(s) that can be used during an outage to supply the critical load(s) assuming the tank were full. It is equal to the total storage volume minus the dead volume and reserved volume.
• Dead volume: The volume of water at the bottom of the tank that, when the water level reaches this level, there is not enough head to supply the system. This level depends on the elevation of the tank(s) and the system pressure requirement. This volume may be nominal but it is important not to include it in the usable tank volume to receive an accurate runtime estimate.
• Reserved volume: Tank volume that must be reserved for emergency fire suppression requirements or similar uses.
• Empty volume: The amount of empty volume at the top of the storage tank before it would be refilled during normal operations. Storage systems could be operated with automatic setpoints, using an automatic control rule to fill from the supply source when the water drops below a certain volume, or with a manual process by the operator. It's not possible to know exactly what the water level will be at the moment of an unexpected outage, so using the greatest typical empty volume that the storage tank could have at any given time will yield a conservative runtime estimate.
Useable Tank Volume
Dead Volume and Reserved Volume
Empty Volume
Onsite Storage Tank Volume Characteristics

## Calculator
Water Redundant System Analysis
Use this worksheet to establish the number of days current redundant systems will be able to meet critical loads.
This format denotes data entry cells.
This format denotes cells that should not be edited.
This format denotes the final value that can be used as an input for TRN, Baseline Development Action 3.
Section 1 inputs are missing. Please enter all required inputs before viewing results.
FINAL REDUNDANT SYSTEM RUNTIME: Return to this value once you have completed the yellow highlighted questions below
|  | #VALUE! | hours | Use this value as an input for "Estimated Run Time (hrs)" in the TRN, Baseline Development Action 3. The maximum modeled runtime relevant for the TRN analysis is 4500 hours.
Section 1 | Required for all systems:
Step | Description | Data Entry & Calculations | Units | Comment
1 | Type of redundant water system |  |  | Select the description that best describes your redundant water system from the dropdown list. An onsite secondary water source could refer to a well or surface water for example. An offsite redundant source, e.g., a regional water tower, must be able to supply the site in the case that the primary source fails. The "System Definitions and Requirements" section in the Introduction tab contains important descriptions of the redundant system types for the purposes of this calculator.
2 | Average daily water load for the system during an outage |  | gallons/ day | This may be larger than the critical load(s) if the redundant system is connected to a larger system including non-critical loads. Account for any loads that will be curtailed during an outage, such as irrigation. If there is no storage tank, check that the supply can meet the peak load, which may be greater than the daily average load.
Section 2 | Only required for onsite storage tank systems:
This section is not required based on your previous inputs.
Step | Description | Data Entry & Calculations | Units | Comment
1 | Useable tank volume |  | gallons | This value is the storage capacity of the tank(s) that can be used during an outage. If there are multiple tanks, treat them as one aggregated system for this section. Be sure to include Dead Volume or Reserved Volume. See Section 6 of the Introduction Tab for more details.
2 | Empty tank volume at any given point in time pre-outage |  | gallons | The amount of empty volume at the top of the storage tank before it would be refilled during normal operations. See Section 6 of the Introduction Tab for more details.
3 | Water loss factor for the piping between the storage tank and the load(s) |  |  | Estimate what the loss factor is based on your knowledge of the piping system. The age of pipes will be the biggest factor (older pipes will leak more, PVC tends to be newer), followed by distance to load (longer distance means more opportunities to leak). If you are unable to estimate this value, a resilience gap strategy could be to conduct a water audit to obtain a precise value and possibly identify the location of leaks to reduce water loss.
Section 3 | Only required for onsite or offsite secondary water sources:
This section is not required based on your previous inputs.
Step | Description | Data Entry & Calculations | Units | Comment
1 | Flow rate that can be provided by the onsite or offsite secondary water source supply |  | gallons/ minute | This information could be provided by the system/pump specifications. Enter the maximum flow rate that the offsite or onsite secondary water system is designed to provide the site.
2 | Water loss factor for the piping between the onsite or offsite secondary water source and the onsite storage tank (if present) or the load(s) (if no storage tank) |  |  | Estimate what the loss factor is based on your knowledge of the piping system. The age of pipes will be the biggest factor (older pipes will leak more, PVC tends to be newer), followed by distance to load (longer distance means more opportunities to leak). If you have no idea, a resilience gap strategy would be to conduct a water audit to obtain a precise value and possibly identify the location of leaks to reduce water loss.
3 | Peak water load for the system during an outage | 0 | gallons/minute | The daily load will likely not be evenly distributed throughout the day, and if there is no storage tank onsite, then the secondary source must meet the peak load to achieve full functionality of the system. If the peak load is known, this cell can be overwritten with that data, but many sites will not have this information. If the peak load cannot be met, in reality there would be partial outages, but the TRN only gives credit for meeting the entire critical load(s). In line with a conservative approach, the estimate provided here assumes a peak load that is 1.5 times as big as the average load.

## Look Up (hidden)
Redundant system types
Onsite storage tank(s) connected only to the primary water supply
Onsite or offsite secondary water source that supplies onsite storage tank(s)
Onsite or offsite secondary water source that directly supplies critical load(s)
Yes |  | Required Sections
No |  | Section 2 | FALSE
|  | Section 3 | FALSE
days
gallons/day |  | Missing Inputs
|  | Section 1 | TRUE
Water Loss Factor |  | Section 2 | TRUE
Very low (0-10%) | 5 | Section 3 | TRUE
Low (10-20%) | 15
Typical (20-30%) | 25 | Runtimes
High (30-40%) | 35 | Storage Runtime (days)
Very high (40-50+%) | 45 | Secondary Supply Runtime (days)
Secondary + Storage Runtime (days)
Water loss factor storage tank | #N/A
Water loss factor secondary supply | #N/A